## Sheet1
Id | Name | Source | Type | MeasuringUnit | Comment | Alarm | AlarmGroup | AlarmText | AlarmLimitMin | AlarmLimitMax | Historian
1 | LSHH_T1 | DB7.DBX0.0 | BOOL | None | LSHH_Tank T1 - Very High Level | True | Alarm | LSHH_Tank T1 - Very High Level | 0 | 1 | False
2 | LSLL_T1 | DB7.DBX0.1 | BOOL | None | LSLL_Tank T1 - Very Low Level | True | Alarm | LSLL_Tank T1 - Very Low Level | 0 | 1 | False
3 | LSHH_T2 | DB7.DBX0.2 | BOOL | None | LSHH_Tank T2 - Very High Level | True | Alarm | LSHH_Tank T2 - Very High Level | 0 | 1 | False
4 | LSLL_T2 | DB7.DBX0.3 | BOOL | None | LSLL_Tank T2 - Very Low Level | True | Alarm | LSLL_Tank T2 - Very Low Level | 0 | 1 | False
5 | LSH_CT | DB7.DBX0.4 | BOOL | None | LSH_Chemicals Tank - High Level | True | Alarm | LSH_Chemicals Tank - High Level | 0 | 1 | False
6 | LSL_CT | DB7.DBX0.5 | BOOL | None | LSL_Chemicals Tank - Low Level | True | Alarm | LSL_Chemicals Tank - Low Level | 0 | 1 | False
7 | AI_1_HHI_ALARM | DB21.DBX22.0 | BOOL | None | Alarm - Very High Level of pH in Tank 2 | True | Alarm | Alarm - Very High Level of pH in Tank 2 | 0 | 1 | False
8 | AI_1_HI_WARN | DB21.DBX22.1 | BOOL | None | Warn - High Level of pH in Tank 2 | True | Alarm | Warn - High Level of pH in Tank 2 | 0 | 1 | False
9 | AI_1_LO_WARN | DB21.DBX22.2 | BOOL | None | Warn - Low Level of pH in Tank 2 | True | Alarm | Warn - Low Level of pH in Tank 2 | 0 | 1 | False
10 | AI_1_LLO_ALARM | DB21.DBX22.3 | BOOL | None | Alarm - Very Low Level of pH in Tank 2 | True | Alarm | Alarm - Very Low Level of pH in Tank 2 | 0 | 1 | False
11 | FI_1_HHI_ALARM | DB19.DBX22.0 | BOOL | None | Alarm - Very High flow in the pipe leading to the tank 2 | True | Alarm | Alarm - Very High flow in the pipe leading to the tank 2 | 0 | 1 | False
12 | FI_1_HI_WARN | DB19.DBX22.1 | BOOL | None | Warn - High flow in the pipe leading to the tank 2 | True | Alarm | Warn - High flow in the pipe leading to the tank 2 | 0 | 1 | False
13 | FI_1_LO_WARN | DB19.DBX22.2 | BOOL | None | Warn - Low flow in the pipe leading to the tank 2 | True | Alarm | Warn - Low flow in the pipe leading to the tank 2 | 0 | 1 | False
14 | FI_1_LLO_ALARM | DB19.DBX22.3 | BOOL | None | Alarm - Very Low flow in the pipe leading to the tank 2 | True | Alarm | Alarm - Very Low flow in the pipe leading to the tank 2 | 0 | 1 | False
15 | FI_2_HHI_ALARM | DB22.DBX22.0 | BOOL | None | Alarm - Very High flow at the end of the line | True | Alarm | Alarm - Very High flow at the end of the line | 0 | 1 | False
16 | FI_2_HI_WARN | DB22.DBX22.1 | BOOL | None | Warn - High flow at the end of the line | True | Alarm | Warn - High flow at the end of the line | 0 | 1 | False
17 | FI_2_LO_WARN | DB22.DBX22.2 | BOOL | None | Warn - Low flow at the end of the line | True | Alarm | Warn - Low flow at the end of the line | 0 | 1 | False
18 | FI_2_LLO_ALARM | DB22.DBX22.3 | BOOL | None | Alarm - Very Low flow at the end of the line | True | Alarm | Alarm - Very Low flow at the end of the line | 0 | 1 | False
19 | LI_1_HHI_ALARM | DB4.DBX22.0 | BOOL | None | Alarm - Very High level in Tank 1 | True | Alarm | Alarm - Very High level in Tank 1 | 0 | 1 | False
20 | LI_1_HI_WARN | DB4.DBX22.1 | BOOL | None | Warn - High level in Tank 1 | True | Alarm | Warn - High level in Tank 1 | 0 | 1 | False
21 | LI_1_LO_WARN | DB4.DBX22.2 | BOOL | None | Warn - Low level in Tank 1 | True | Alarm | Warn - Low level in Tank 1 | 0 | 1 | False
22 | LI_1_LLO_ALARM | DB4.DBX22.3 | BOOL | None | Alarm - Very Low level in Tank 1 | True | Alarm | Alarm - Very Low level in Tank 1 | 0 | 1 | False
23 | LI_2_HHI_ALARM | DB20.DBX22.0 | BOOL | None | Alarm - Very High level in Tank 2 | True | Alarm | Alarm - Very High level in Tank 2 | 0 | 1 | False
24 | LI_2_HI_WARN | DB20.DBX22.1 | BOOL | None | Warn - High level in Tank 2 | True | Alarm | Warn - High level in Tank 2 | 0 | 1 | False
25 | LI_2_LO_WARN | DB20.DBX22.2 | BOOL | None | Warn - Low level in Tank 2 | True | Alarm | Warn - Low level in Tank 2 | 0 | 1 | False
26 | LI_2_LLO_ALARM | DB20.DBX22.3 | BOOL | None | Alarm - Very Low level in Tank 2 | True | Alarm | Alarm - Very Low level in Tank 2 | 0 | 1 | False
27 | P1_FAULT | DB8.DBX18.5 | BOOL | None | Pump P1 - Fault | True | Alarm | Pump P1 - Fault | 0 | 1 | False
28 | P1_STATE | DB8.DBW28 | INT | None | Pump P1 - State | False |  | Pump P1 - Fault | 0 | 1 | False
29 | P2_FAULT | DB9.DBX18.5 | BOOL | None | Pump P2 - Fault | True | Alarm | Pump P2 - Fault | 0 | 1 | False
30 | P2_STATE | DB9.DBW28 | INT | None | Pump P2 - State | False |  | Pump P2 - State | 0 | 1 | False
31 | P3_FAULT | DB15.DBX18.5 | BOOL | None | Pump P3 - Fault | True | Alarm | Pump P3 - Fault | 0 | 1 | False
32 | P3_STATE | DB15.DBW28 | INT | None | Pump P3 - State | False |  | Pump P3 - State | 0 | 1 | False
33 | UV_1_FAULT | DB10.DBX12.4 | BOOL | None | UV_1 - Fault | True | Alarm | UV_1 - Fault | 0 | 1 | False
34 | UV_1_STATE | DB10.DBW14 | INT | None | UV_1 - State | False |  | UV_1 - State | 0 | 1 | False
35 | UV_2_FAULT | DB11.DBX12.4 | BOOL | None | UV_2 - Fault | True | Alarm | UV_2 - Fault | 0 | 1 | False
36 | UV_2_STATE | DB11.DBW14 | INT | None | UV_2 - State | False |  | UV_2 - State | 0 | 1 | False
37 | AI_1 | DB29.DBD20.0 | REAL | pH | Ph in Tank 3 | False |  |  | 0 | 1 | True
38 | FI_1 | DB5.DBD20.0 | REAL | m3/h | Flow in the pipe leading to the tank 2 | False |  |  | 0 | 1 | True
39 | FI_2 | DB30.DBD20.0 | REAL | m3/h | Flow at the end of the line | False |  |  | 0 | 1 | True
40 | LI_1 | DB23.DBD8.0 | REAL | % | Tank 1 Level | False |  |  | 0 | 1 | True
41 | LI_2 | DB6.DBD8.0 | REAL | % | Tank 2 Level | False |  |  | 0 | 1 | True
42 | UV_1_AM | DB10.DBX12.6 | BOOL | None | 0 - Auto, 1 - Manual | False |  |  | 0 | 1 | False
43 | UV_2_AM | DB11.DBX12.6 | BOOL | None | 0 - Auto, 1 - Manual | False |  |  | 0 | 1 | False
44 | UV_1_OPEN | DB10.DBX12.0 | BOOL | Send | Open valve UV1 signal from scada | False |  |  | 0 | 1 | False
45 | UV_1_CLOSE | DB10.DBX12.1 | BOOL | Send | Close valve UV1 signal from scada | False |  |  | 0 | 1 | False
46 | UV_2_OPEN | DB11.DBX12.0 | BOOL | Send | Open valve UV1 signal from scada | False |  |  | 0 | 1 | False
47 | UV_2_CLOSE | DB11.DBX12.1 | BOOL | Send | Close valve UV2 signal from scada | False |  |  | 0 | 1 | False
48 | UV_1_BLOCKADE | DB10.DBX12.5 | BOOL | None | 0 - Close, 1 - Open | False |  |  | 0 | 1 | False
49 | UV_2_BLOCKADE | DB11.DBX12.5 | BOOL | None | 0 - Close, 1 - Open | False |  |  | 0 | 1 | False
50 | UV_1_AUTO | DB10.DBX12.2 | BOOL | Send | UV1 Auto mode signal from scada | False |  |  | 0 | 1 | False
51 | UV_1_MANUAL | DB10.DBX12.3 | BOOL | Send | UV1 Manual mode signal from scada | False |  |  | 0 | 1 | False
52 | UV_2_AUTO | DB11.DBX12.2 | BOOL | Send | UV2 Auto mode signal from scada | False |  |  | 0 | 1 | False
53 | UV_2_MANUAL | DB11.DBX12.3 | BOOL | Send | UV2 Manual mode signal from scada | False |  |  | 0 | 1 | False
54 | FILL_T1_START | DB12.DBX0.0 | BOOL | Send | Filling T1 - Start signal from SCADA | False |  |  | 0 | 1 | False
55 | TEST | DB2.DBD0 | REAL | None | Test | False |  |  | 0 | 1 | False
56 | P1_AUTO | DB8.DBX18.2 | BOOL | Send | Auto mode signal from Scada | False |  |  | 0 | 1 | False
57 | P1_MANUAL | DB8.DBX18.3 | BOOL | Send | Manual mode signal from Scada | False |  |  | 0 | 1 | False
58 | P1_START | DB8.DBX18.0 | BOOL | Send | Start signal from Scada | False |  |  | 0 | 1 | False
59 | P1_STOP | DB8.DBX18.1 | BOOL | Send | Stop signal from Scada | False |  |  | 0 | 1 | False
60 | P1_BLOCKADE | DB8.DBX18.4 | BOOL | None | 0 - blockade unactive, 1 - blockade active | False |  |  | 0 | 1 | False
61 | P1_RUN_H | DB8.DBW20 | INT | None | Running time - hours | False |  |  | 0 | 1 | False
62 | P1_RUN_M | DB8.DBW22 | INT | None | Running time - minutes | False |  |  | 0 | 1 | False
63 | P1_RUN_S | DB8.DBW24 | INT | None | Running time - seconds | False |  |  | 0 | 1 | False
64 | P1_SP | DB8.DBD30 | REAL | Send | Setpoint value [%] | False |  |  | 0 | 1 | False
65 | P1_PV | DB8.DBD34 | REAL | None | Acctual speed [%] | False |  |  | 0 | 1 | True
66 | P1_MODE | DB8.DBX26.1 | BOOL | None | 0 - auto, 1 - manual (Scada) | False |  |  | 0 | 1 | False
67 | P2_AUTO | DB9.DBX18.2 | BOOL | Send | Auto mode signal from Scada | False |  |  | 0 | 1 | False
68 | P2_MANUAL | DB9.DBX18.3 | BOOL | Send | Manual mode signal from Scada | False |  |  | 0 | 1 | False
69 | P2_START | DB9.DBX18.0 | BOOL | Send | Start signal from Scada | False |  |  | 0 | 1 | False
70 | P2_STOP | DB9.DBX18.1 | BOOL | Send | Stop signal from Scada | False |  |  | 0 | 1 | False
71 | P2_BLOCKADE | DB9.DBX18.4 | BOOL | None | 0 - blockade unactive, 1 - blockade active | False |  |  | 0 | 1 | False
72 | P2_RUN_H | DB9.DBW20 | INT | None | Running time - hours | False |  |  | 0 | 1 | False
73 | P2_RUN_M | DB9.DBW22 | INT | None | Running time - minutes | False |  |  | 0 | 1 | False
74 | P2_RUN_S | DB9.DBW24 | INT | None | Running time - seconds | False |  |  | 0 | 1 | False
75 | P2_SP | DB9.DBD30 | REAL | Send | Setpoint value [%] | False |  |  | 0 | 1 | False
76 | P2_PV | DB9.DBD34 | REAL | None | Acctual speed [%] | False |  |  | 0 | 1 | True
77 | P2_MODE | DB9.DBX26.1 | BOOL | None | 0 - auto, 1 - manual (Scada) | False |  |  | 0 | 1 | False
78 | P3_AUTO | DB15.DBX18.2 | BOOL | Send | Auto mode signal from Scada | False |  |  | 0 | 1 | False
79 | P3_MANUAL | DB15.DBX18.3 | BOOL | Send | Manual mode signal from Scada | False |  |  | 0 | 1 | False
80 | P3_START | DB15.DBX18.0 | BOOL | Send | Start signal from Scada | False |  |  | 0 | 1 | False
81 | P2_STOP | DB15.DBX18.1 | BOOL | Send | Stop signal from Scada | False |  |  | 0 | 1 | False
82 | P3_BLOCKADE | DB15.DBX18.4 | BOOL | None | 0 - blockade unactive, 1 - blockade active | False |  |  | 0 | 1 | False
83 | P3_RUN_H | DB15.DBW20 | INT | None | Running time - hours | False |  |  | 0 | 1 | False
84 | P3_RUN_M | DB15.DBW22 | INT | None | Running time - minutes | False |  |  | 0 | 1 | False
85 | P3_RUN_S | DB15.DBW24 | INT | None | Running time - seconds | False |  |  | 0 | 1 | False
86 | P3_SP | DB15.DBD30 | REAL | Send | Setpoint value [%] | False |  |  | 0 | 1 | False
87 | P3_PV | DB15.DBD34 | REAL | None | Acctual speed [%] | False |  |  | 0 | 1 | True
88 | P3_MODE | DB15.DBX26.1 | BOOL | None | 0 - auto, 1 - manual (Scada) | False |  |  | 0 | 1 | False
89 | TestInt | DB2.DBW4 | INT | None | Test | False |  |  | 0 | 1 | False
90 | FILL_T1_START | DB12.DBX0.0 | BOOL | Send | Start filling signal from SCADA | False |  |  | 0 | 1 | False
91 | FILL_T1_STOP | DB12.DBX0.2 | BOOL | Send | Stop filling signal from SCADA | False |  |  | 0 | 1 | False
92 | FILL_T1_STATE | DB12.DBW2 | INT | None | 0 - Stop, 1 - Filling T1, 2 - No conditions to run | False |  |  | 0 | 1 | False
93 | TRANSFER_TO_T2_START | DB18.DBX0.0 | BOOL | Send | Start transfer to T2 signal from SCADA | False |  |  | 0 | 1 | False
94 | TRANSFER_TO_T2_STOP | DB18.DBX0.2 | BOOL | Send | Stop transfer to T2 signal from SCADA | False |  |  | 0 | 1 | False
95 | TRANSFER_TO_T2_STATE | DB18.DBW10 | INT | None | 0 - Stop, 1 - Transfer to T2, 2 - Adding chemicals, 3 - No conditions to run | False |  |  | 0 | 1 | False
95 | TRANSFER_TO_T2_P1_SP | DB18.DBD12 | REAL | Send | Pump P1 Speed Setpoint [%] | False |  |  | 0 | 1 | False
95 | DOSE_CHEMICALS_START | DB24.DBX0.0 | BOOL | Send | Start dosing chemicals signal from SCADA | False |  |  | 0 | 1 | False
95 | DOSE_CHEMICALS_STOP | DB24.DBX0.2 | BOOL | Send | Stop dosing chemicals to T2 signal from SCADA | False |  |  | 0 | 1 | False
95 | DOSE_CHEMICALS_STATE | DB24.DBW2 | INT | None | 0 - Stop, 1 - Adding Chemicals, 2 - No conditions to run | False |  |  | 0 | 1 | False
95 | EMPTYING_T2_START | DB27.DBX0.0 | BOOL | Send | Start emptying T2 signal from SCADA | False |  |  | 0 | 1 | False
95 | EMPTYING_T2_STOP | DB27.DBX0.2 | BOOL | Send | Stop emptying T2 signal from SCADA | False |  |  | 0 | 1 | False
95 | EMPTYING_T2_STATE | DB27.DBW2 | INT | None | 0 - Stop, 1 - Adding Chemicals, 2 - No conditions to run | False |  |  | 0 | 1 | False
95 | EMPTYING_T2_P2_SP | DB27.DBD4 | REAL | Send | Pump P2 Speed Setpoint [%] | False |  |  | 0 | 1 | False